## Slide 1: 2 MW/ 4MW-hr Storage system SRJ 2012
Technical Challenges of high level of inverter-based resources in Power System
NSF Workshop on Power Electronics-enabled
Operation of Power Systems
31 October 2019
Bob Lasseter
University of Wisconsin- Madison
Notes: Example of DER describe: Fuel cell, PV large battery
DER penetration
1000 10,000 or more how do we handle, control ?
Are they a problem or can they bring value?
Cluster in to a microgrid

## Slide 2: High level of inverter-based resources
California ~50% Peak Wind & PV Instant. Penetration
Texas ~55% Peak Wind Instant. Penetration
Hawaii Island ~70% Peak PV Instantaneous Penetration
M. Elkhatib, R. Lasseter, Wei Du, “Evaluation of Inverter-based Grid Frequency Support using Frequency-Watt and Grid-Forming PV Inverters,” IEEE PES 2018
Hawaiian island of Oahu
(50% distributed PV)
Total system load
Load tripping

## Slide 3
Time(s)
Time(s)
Frequency (Hz)
Grid-following
(Frequency-Watt)
5% loss of load
“Loss of inertia in power system”

## Slide 4
Time(s)
Time(s)
Time(s)
Time(s)
Frequency (Hz)
Frequency (Hz)
Grid-following
Grid-forming
Loss of inertia??

## Slide 5
Grid Following Control (GFL)
Frequency is measured; Control P & Q
Controls Real & Reactive power
Frequency-Watt Function (grid support)
Dependent on utility for voltage No direct control of frequency Re-dispatch for load changes
Grid Forming Control (GFM)
P & Q is measured; Control Voltage & Frequency
Controls Voltage and Frequency
Droop Control (Autonomous power sharing)
No direct control of current No direct control of Q
Inverter control

## Slide 6: High level of inverter-based resources
  Major Questions
  Large turbine - Inverter dynamics?
  How do you control hundreds of thousands to millions of inverters?

## Slide 7
Turbine - Inverter dynamics
Model of the mixed source (GFM or GFL)
X: penetration
Generator parameters | 
TA = 8s | = 377 rad/s
TB = 0.9s | = 3.5 s/pu
Mp,gen = 0.05ωs /pu | 
Generator parameters | 
TA = 8s | 
TB = 0.9s | 
Mp,gen = 0.05ωs /pu | 
GFL parameters
Mp,inv = 0.05ωs /pu
TL = 0.5s
GFM parameters
Mp,inv = 0.05ωs /pu
TM = 7.96 ms

## Slide 8
GFM Inverters Increases Damping in Power System

## Slide 9: High level of inverter-based resources
  Major Questions
  Large turbine - Inverter dynamics?
  How do you control hundreds of thousands to millions of inverters?
  Autonomous frequency stabilization
  Autonomous relief of overloaded GFM inverters
  Implementation of GFM PV systems with autonomous reserves

## Slide 10
Autonomous Power sharing
Overload
  A1 near rating so that A1 + > rating
A1
A2
Grid-forming Inverters

## Slide 11
Overload
Change the phase angle
between sources: Dd
A1
A2

## Slide 12
Overload Transfer
Change the phase angle
between sources: Dd
A1
A2

## Slide 13
G
PV- Inverter and Turbine
Loss of load
Pmax = MPP

## Slide 14
G
PV- Inverter and Turbine
Loss of 25 MW

## Slide 15
PV- Inverter and Turbine
with Reserves

## Slide 16
Estimate MPP voltage
to provide Reserves
Reserve
Actual PV MPP vs. Estimation of MPP

## Slide 17
Load Sharing
Different droops

## Slide 18
Over load protection for thousands of GFM inverters
Use of different droops in the distribution system
Voltage stability and reactive power flow
Modeling and simulation tools
System protection
Inverter fault ride-through
Allocation and data for inverter reserves
Research Questions